## SWSTP Sample Monitoring data
H a w k e s b u r y C i t y C o u n c i l
366 George Street (PO Box 146) Windsor NSW 2756 DX 8601 WINDSOR
Phone: (02) 4560 4444 Facsimilie: (02) 4587 7740 Email:council@hawkesbury.nsw.gov.au
South Windsor Sewage Treatment Plant Monitoring Data
EPA License number: |  |  | 3306 |  |  |  |  | Monitoring Point: | EPA 2, V-notch weir (discharge into South Creek)
License website link: |  | https://www.hawkesbury.nsw.gov.au/link/pollution-monitoring-data-swstp |  |  |  |  | Sampling Frequency: |  | Fortnightly
| Licensee: |  | Hawkesbury City Council |  |  |  |  | Premises: | Fairey Road South Windsor NSW
Note: Uncontrolled document when printed
Reporting Year | Sampled Date | Obtained Date | Published Date | Pollutant
|  |  |  | Biological Oxygen Demand (BOD) mg/L | Total Suspended Solids (TSS) mg/L | Nitrogen (ammonia) (mg/L | Faecal Coliforms (colony forming units per 100 mL) | Phosphorus (total) mg/L | Nitrogen (total) mg/L | pH | Total Kjeldahl Nitrogen (TKN) mg/L | Nitrate+nitrite (Oxidised Nitrogen) mg/L | Oil & Grease mg/L
|  |  |  | Limit: 50 %ile = 7 90%ile = 10 | Limit: 50 %ile = 10 90%ile = 15 | Limit: 50 %ile = 1.5 90%ile = 2 | Limit: 50 %ile = 150 90%ile = 200 | Limit: 50 %ile = 0.2 90%ile = 0.3 | Limit: 50 %ile = 7 90%ile = 10 | Limit: 6.5-8.5 | Limit: N/A | Limit: N/A | Limit: 100%ile = 10
2020 / 2021 | 2020-07-02 | 2020-07-10 | 2020-08-14 | 1 | 2.5 | 0.02 | 0.5 | 0.18 | 3 | 7.24 | 0.7 | 2.33 | 1
| 2020-07-16 | 2020-07-24 | 2020-08-15 | 1 | 2.5 | 0.005 | 0.5 | 0.02 | 3.2 | 7.78 | 0.9 | 2.26 | 2.5
| 2020-07-30 | 2020-08-10 | 2020-08-16 | 1 | 2.5 | 3.72 | 1 | 0.005 | 7.2 | 7.75 | 4.7 | 2.47 | 5
| 2020-08-13 | 2020-08-20 | 2020-09-15 | 5 | 2.5 | 1.56 | 25 | 0.06 | 6.1 | 7.59 | 2.9 | 3.24 | 2.5
| 2020-08-24 | 2020-08-31 | 2020-09-15 | 1 | 2.5 | 0.04 | 10 | 0.1 | 4.2 | 7.53 | 1.2 | 2.96 | 2.5
| 2020-09-07 | 2020-09-15 | 2020-10-14 | 4 | 8 | 0.11 | 50 | 0.12 | 1.7 | 7.76 | 1.4 | 0.29 | 2.5
| 2020-09-21 | 2020-09-28 | 2020-10-14 | 1 | 2.5 | 0.04 | 1 | 0.09 | 1.4 | 7.81 | 1 | 0.38 | 2.5
| 2020-10-01 | 2020-10-09 | 2020-11-12 | 4 | 2.5 | 0.06 | 4 | 0.06 | 1.1 | 7.54 | 1.1 | 0.005 | 2.5
| 2020-10-12 | 2020-10-19 | 2020-11-12 | 1 | 2.5 | 0.07 | 8 | 0.08 | 1.2 | 7.84 | 0.9 | 0.32 | 2.5
| 2020-10-26 | 2020-11-02 | 2020-11-12 | 3 | 7 | 0.14 | 1300 | 0.12 | 2.7 | 7.79 | 1.1 | 1.61 | 2.5
| 2020-11-09 | 2020-11-16 | 2020-12-09 | 2 | 8 | 0.03 | 150 | 0.09 | 0.7 | 7.2 | 0.4 | 0.26 | 2.5
| 2020-11-23 | 2020-11-30 | 2020-12-09 | 3 | 2.5 | 0.11 | 3500 | 0.26 | 0.9 | 7.97 | 0.9 | 0.04 | 2.5
| 2020-12-07 | 2020-12-14 | 2021-01-19 | 2 | 12 | 0.03 | 0.5 | 0.12 | 0.7 | 7.7 | 0.7 | 0.03 | 2.5
| 2020-12-21 | 2021-01-04 | 2021-01-19 | 1 | 20 | 0.06 | 48 | 0.21 | 1.2 | 7.59 | 1.2 | 0.005 | 2.5
| 2021-01-04 | 2021-01-12 | 2021-02-11 | 1 | 10 | 0.62 | 0.5 | 0.02 | 0.8 | 7.2 | 0.8 | 0.03 | 2.5
| 2021-01-18 | 2021-01-28 | 2021-02-11 | 5 | 2.5 | 0.1 | 38 | 0.07 | 1 | 7.71 | 1 | 0.005 | 2.5
| 2021-02-01 | 2021-02-09 | 2021-03-10 | 2 | 2.5 | 0.03 | 0.5 | 0.38 | 0.7 | 7.02 | 0.7 | 0.005 | 2.5
| 2021-02-15 | 2021-02-23 | 2021-03-10 | 1 | 2.5 | 0.08 | 0.5 | 0.2 | 1.5 | 7 | 0.8 | 0.71 | 2.5
| 2021-03-01 | 2021-03-08 | 2021-04-09 | 1 | 7 | 0.01 | 77 | 0.11 | 0.5 | 8 | 0.4 | 0.12 | 2.5
| 2021-03-15 | 2021-03-22 | 2021-04-09 | 3 | 6 | 0.14 | 0.5 | 0.05 | 0.8 | 7.58 | 0.7 | 0.07 | 2.5
| 2021-03-29 | 2021-04-07 | 2021-04-09 | 6 | 8 | 1.43 | 200 | 0.42 | 1.8 | 7.77 | 1.8 | 0.005 | 2.5
| 2021-04-12 | 2021-04-19 | 2021-05-07 | 6 | 2.5 | 0.8 | 2 | 0.12 | 1.3 | 7.79 | 1.3 | 0.005 | 6
| 2021-04-26 | 2021-05-04 | 2021-05-07 | 4 | 2.5 | 0.03 | 2 | 0.06 | 0.7 | 6.97 | 0.7 | 0.02 | 2.5
| 2021-05-11 | 2021-05-19 | 2021-06-11 | 11 | 2.5 | 0.04 | 0.5 | 0.06 | 0.6 | 7.61 | 0.6 | 0.01 | 2.5
| 2021-05-24 | 2021-05-31 | 2021-06-11 | 10 | 2.5 | 0.03 | 0.5 | 0.03 | 0.6 | 7.59 | 0.6 | 0.02 | 6
| 2021-06-07 | 2021-06-15 | 2021-07-13 | 3 | 6 | 0.03 | 0.5 | 0.06 | 0.6 | 7.41 | 0.6 | 0.005 | 2.5
| 2021-06-21 | 2021-06-28 | 2021-07-13 | 19 | 6 | 0.03 | 0.5 | 0.03 | 0.7 | 7.39 | 0.7 | 0.04 | 2.5
Comments:
July 2020 - All data within license limits
August 2020 - All data within license limits
September 2020 - All data within license limits
October 2020 - All data within license limits
November 2020 - All data within license limits
December 2020 - All data within license limits
January 2021 - All data within license limits
February 2021 - All data within license limits
March 2021 - All data within license limits
April 2021 - All data within license limits
May 2021 - All data within license limits
June 2021 - All data within license limits
2021 / 2022 | 2021-07-05 | 2021-07-12 | 2021-08-11 | 2 | 2.5 | 0.02 | 0.5 | 0.06 | 1.4 | 6.97 | 1.4 | 0.005 | 2.5
| 2021-07-19 | 2021-07-26 | 2021-08-11 | 3 | 2.5 | 0.01 | 0.5 | 0.07 | 3 | 7.63 | 1.1 | 1.88 | 2.5
| 2021-08-02 | 2021-08-09 | 2021-09-16 | 16 | 5 | 0.16 | 0.5 | 0.06 | 1 | 7.55 | 1 | 0.04 | 2.5
| 2021-08-16 | 2021-08-24 | 2021-09-16 | 11 | 5 | 0.16 | 0.5 | 0.1 | 1.4 | 7.71 | 1.1 | 0.29 | 2.5
| 2021-08-30 | 2021-09-06 | 2021-09-16 | 2 | 18 | 0.1 | 0.5 | 0.2 | 6.4 | 7.38 | 1.7 | 4.66 | 2.5
| 2021-09-13 | 2021-09-22 | 2021-10-15 | 1 | 15 | 0.19 | 0.5 | 0.06 | 3.2 | 7.3 | 1.6 | 1.65 | 2.5
| 2021-09-27 | 2021-10-05 | 2021-10-15 | 1 | 18 | 0.12 | 2 | 0.005 | 2.2 | 7.31 | 0.8 | 1.38 | 2.5
| 2021-10-11 | 2021-10-18 | 2021-11-10 | 1 | 2.5 | 0.02 | 0.5 | 0.04 | 4.6 | 7.8 | 1.3 | 3.3 | 2.5
| 2021-10-25 | 2021-11-02 | 2021-11-10 | 3 | 8 | 0.05 | 1 | 0.31 | 1 | 7.85 | 0.9 | 0.11 | 2.5
| 2021-11-08 | 2021-11-15 | 2021-12-14 | 1 | 2.5 | 0.2 | 0.5 | 0.09 | 3.6 | 7.36 | 1.1 | 2.52 | 2.5
| 2021-11-22 | 2021-11-29 | 2021-12-14 | 2 | 2.5 | 0.04 | 1 | 0.11 | 5.1 | 7.77 | 1.6 | 3.49 | 2.5
| 2021-12-06 | 2021-12-14 | 2022-01-26 | 16 | 2.5 | 0.04 | 0.5 | 0.09 | 0.6 | 7.95 | 0.6 | 0.005 | 2.5
| 2021-12-20 | 2021-12-31 | 2022-01-26 | 1 | 2.5 | 0.17 | 0.5 | 0.08 | 0.8 | 7.67 | 0.8 | 0.03 | 2.5
| 2021-12-31 | 2022-01-10 | 2022-01-26 | 1 | 2.5 | 0.1 | 1 | 0.1 | 1.2 | 7.99 | 1 | 0.18 | 2.5
| 2022-01-14 | 2022-01-24 | 2022-01-21 | 1 | 6 | 0.06 | 0.5 | 0.2 | 0.4 | 7.21 | 0.4 | 0.02 | 2.5
| 2022-01-25 | 2022-02-02 | 2022-11-21 | 3 | 2.5 | 0.12 | 3 | 0.11 | 2.7 | 8.11 | 1.1 | 1.61 | 2.5
| 2022-02-07 | 2022-02-14 | 2022-03-18 | 4 | 2.5 | 0.08 | 0.5 | 0.32 | 2.6 | 7.41 | 0.6 | 2.01 | 2.5
| 2022-02-21 | 2022-02-28 | 2022-03-18 | 1 | 2.5 | 0.13 | 0.5 | 0.13 | 0.7 | 7.73 | 0.6 | 0.11 | 2.5
| 2022-03-07 | 2022-03-21 | 2022-04-19 | 1 | 2.5 | 0.04 | 0.5 | 0.27 | 1.2 | 7.63 | 0.5 | 0.65 | 2.5
| 2022-03-21 | 2022-03-29 | 2022-04-19 | 1 | 2.5 | 0.1 | 0.5 | 0.05 | 1.7 | 8.1 | 0.7 | 1.03 | 2.5
| 2022-04-04 | 2022-04-11 | 2022-05-23 | 2 | 2.5 | 0.16 | 0.5 | 0.16 | 4.6 | 7.92 | 1.2 | 3.37 | 2.5
| 2022-04-14 | 2022-04-26 | 2022-05-23 | 1 | 2.5 | 0.04 | 0.5 | 0.06 | 6.1 | 7.61 | 1.2 | 4.89 | 2.5
| 2022-04-26 | 2022-05-05 | 2022-05-23 | 2 | 9 | 0.06 | 0.5 | 0.66 | 2.1 | 7.72 | 1.3 | 0.78 | 2.5
| 2022-05-09 | 2022-05-16 | 2022-06-20 | 1 | 10 | 0.03 | 0.5 | 0.41 | 3.6 | 8.03 | 1.2 | 2.39 | 2.5
| 2022-05-23 | 2022-05-31 | 2022-06-20 | 2 | 11 | 0.02 | 0.5 | 0.65 | 2.6 | 8.07 | 1.2 | 1.43 | 2.5
| 2022-06-06 | 2022-06-14 | 2022-07-18 | 11 | 8 | 0.04 | 0.5 | 0.02 | 3.4 | 7.92 | 1.1 | 2.25 | 2.5
| 2022-06-20 | 2022-06-27 | 2022-07-18 | 19 | 14 | 0.04 | 0.5 | 0.22 | 1.1 | 7.43 | 1.1 | 0.04 | 2.5
Comments:
July 2021 - All data within license limits
Aug 2021- All data within license limits
Sep 2021 -All data within license limits
October 2021 -All data within license limits
November 2021 - All data within license limits
December 2021 - -All data within license limits
January 2022 -All data within license limits
February 2022 - All data within license limits
March 2022 - All data within license limits
April 2022 - All data within license limits
May 2022 - All data within license limits
1/06/2022 -All data within license limits except BOD
2022 / 2023 | 2022-07-11 | 2022-07-19 | 2022-08-19 | 11 | 8 | 0.99 | 1 | 0.14 | 3.8 | 7.25 | 2.1 | 1.69 | 2.5
| 2022-07-25 | 2022-08-01 | 2022-08-19 | 6 | 2.5 | 0.02 | 0.5 | 0.05 | 0.8 | 7.73 | 0.8 | 0.02 | 2.5
| 2022-08-08 | 2022-08-16 | 2022-09-14 | 7 | 2.5 | 0.05 | 0.5 | 0.03 | 0.8 | 7.6 | 0.8 | 0.05 | 2.5
| 2022-08-22 | 2022-08-29 | 2022-09-14 | 4 | 2.5 | 0.03 | 0.5 | 0.03 | 1.1 | 7.68 | 0.8 | 0.3 | 2.5
| 2022-09-05 | 2022-09-13 | 2022-10-14 | 7 | 17 | 0.06 | 0.5 | 0.1 | 1.1 | 7.83 | 0.8 | 0.34 | 2.5
| 2022-09-19 | 2022-09-29 | 2022-10-14 | 5 | 2.5 | 0.02 | 0.5 | 0.05 | 2 | 7.74 | 1.1 | 2 | 2.5
| 2022-10-04 | 2022-10-11 | 2022-11-18 | 1 | 2.5 | 0.04 | 0.5 | 0.04 | 1.1 | 7.68 | 0.8 | 0.3 | 2.5
| 2022-10-17 | 2022-10-31 | 2022-11-18 | 3 | 2.5 | 0.1 | 0.5 | 0.02 | 0.8 | 7.86 | 0.8 | 0.04 | 2.5
| 2022-10-31 | 2022-11-07 | 2022-11-18 | 1 | 2.5 | 0.02 | 0.5 | 0.07 | 3 | 7.67 | 0.8 | 2.23 | 2.5
| 2022-11-14 | 2022-11-21 | 2022-12-09 | 1 | 2.5 | 0.07 | 0.5 | 0.05 | 5.5 | 7.9 | 1.3 | 4.18 | 2.5
| 2022-11-28 | 2022-12-05 | 2022-12-09 | 3 | 2.5 | 0.14 | 0.5 | 0.11 | 1.5 | 7.97 | 1.2 | 0.28 | 2.5
| 2022-12-12 | 2022-12-19 | 2023-01-20 | 1 | 2.5 | 0.2 | 0.5 | 0.06 | 1.9 | 8.14 | 1 | 0.94 | 5
| 2022-12-22 | 2023-01-06 | 2023-01-20 | 1 | 2.5 | 0.2 | 0.5 | 0.08 | 1.6 | 7.95 | 1.2 | 0.38 | 2.5
| 2023-01-03 | 2023-01-10 | 2023-02-20 | 3 | 2.5 | 0.1 | 1 | 0.07 | 1 | 7.99 | 1 | 0.005 | 2.5
| 2023-01-16 | 2023-01-23 | 2023-02-20 | 3 | 2.5 | 0.13 | 0.5 | 0.07 | 1 | 7.7 | 1 | 0.04 | 2.5
| 2023-01-30 | 2023-02-06 | 2023-02-20 | 1 | 2.5 | 0.72 | 0.5 | 0.16 | 8.2 | 6.85 | 3.8 | 4.38 | 2.5
| 2023-02-13 | 2023-02-21 | 2023-03-20 | 1 | 2.5 | 0.17 | 0.5 | 0.08 | 0.8 | 7.76 | 0.8 | 0.02 | 2.5
| 2023-02-27 | 2023-03-07 | 2023-03-20 | 4 | 2.5 | 0.23 | 0.5 | 0.12 | 1.3 | 7.74 | 1.2 | 0.07 | 2.5
| 2023-03-13 | 2023-03-20 | 2023-04-14 | 4 | 6 | 0.13 | 0.5 | 0.03 | 0.7 | 7.81 | 0.6 | 0.08 | 2.5
| 2023-03-27 | 2023-04-03 | 2023-04-14 | 8 | 2.5 | 0.07 | 0.5 | 0.06 | 0.7 | 7.35 | 0.7 | 0.02 | 2.5
| 2023-04-06 | 2023-04-17 | 2023-05-15 | 3 | 2.5 | 0.2 | 0.5 | 0.08 | 1.3 | 7.4 | 1.2 | 0.9 | 2.5
| 2023-04-17 | 2023-04-26 | 2023-05-15 | 2 | 2.5 | 0.07 | 0.5 | 0.06 | 0.7 | 7.64 | 0.7 | 0.005 | 2.5
| 2023-05-01 | 2023-05-08 | 2023-06-14 | 1 | 2.5 | 0.06 | 0.5 | 0.03 | 0.5 | 7.51 | 0.4 | 0.12 | 2.5
| 2023-05-15 | 2023-05-22 | 2023-06-14 | 1 | 2.5 | 0.06 | 0.5 | 0.02 | 0.6 | 7.13 | 0.5 | 0.1 | 2.5
| 2023-05-29 | 2023-06-05 | 2023-06-14 | 1 | 2.5 | 0.12 | 0.5 | 0.03 | 1.1 | 7.35 | 0.7 | 0.4 | 2.5
| 2023-06-13 | 2023-06-20 | 2023-07-19 | 1 | 2.5 | 0.03 | 0.5 | 0.01 | 0.6 | 7.26 | 0.6 | 0.04 | 2.5
| 2023-06-26 | 2023-07-03 | 2023-07-19 | 2 | 2.5 | 0.06 | 0.5 | 0.04 | 0.9 | 6.97 | 0.7 | 0.22 | 2.5
Comments:
July 2022 - All data within license limits (Note: Sample was not able to be collected on the due sampling day on 4/7/2022 with access issues to the site due to Flood)
Aug 2022- All data within license limits
Sep 2022 - All data within license limits
October 2022 - All data within license limits
November 2022 - All data within license limits
December 2022 - All data within license limits
January 2023 - All data within license limits
February 2023 - All data within license limits
March 2023 - All data within license limits
April 2023 - All data within license limits
May 2023 - All data within license limits
June 2023 - All data within license limits
2023 / 2024 | 2023-07-10 | 2023-07-17 | 2023-08-18 | 1 | 2.5 | 0.08 | 0.5 | 0.005 | 1.5 | 7.22 | 0.8 | 0.69 | 2.5
| 2023-07-24 | 2023-07-31 | 2023-08-18 | 4 | 2.5 | 0.14 | 0.5 | 0.05 | 1 | 7.42 | 0.8 | 0.23 | 2.5
| 2023-08-07 | 2023-08-14 | 2023-09-15 | 1 | 2.5 | 0.09 | 1 | 0.2 | 2.2 | 7.4 | 1 | 1.16 | 6
| 2023-08-21 | 2023-08-28 | 2023-09-15 | 1 | 2.5 | 0.1 | 0.5 | 0.05 | 1.7 | 7.65 | 0.9 | 0.8 | 2.5
| 2023-09-04 | 2023-09-11 | 2023-10-16 | 1 | 2.5 | 0.08 | 0.05 | 0.04 | 9.4 | 7.53 | 1.4 | 8.05 | 2.5
| 2023-09-18 | 2023-09-26 | 2023-10-16 | 1 | 2.5 | 0.04 | 0.05 | 0.08 | 6.1 | 7.36 | 1.2 | 4.87 | 2.5
| 2023-10-02 | 2023-10-11 | 2023-11-15 | 1 | 2.5 | 0.03 | 0.5 | 0.02 | 5.9 | 7.41 | 1.2 | 4.7 | 2.5
| 2023-10-16 | 2023-10-23 | 2023-11-15 | 1 | 2.5 | 0.03 | 0.5 | 0.05 | 6.1 | 7.46 | 1.4 | 4.71 | 8
| 2023-10-30 | 2023-11-06 | 2023-11-15 | 1 | 6 | 0.005 | 6 | 0.2 | 6.5 | 7.05 | 1.1 | 5.36 | 2.5
| 2023-11-13 | 2023-11-20 | 2023-12-18 | 1 | 2.5 | 0.02 | 0.5 | 0.1 | 6.8 | 7.56 | 1.5 | 5.34 | 2.5
| 2023-11-27 | 2023-12-04 | 2023-12-18 | 1 | 2.5 | 0.005 | 0.5 | 0.17 | 6.5 | 7 | 1.5 | 5.02 | 2.5
| 2024-12-11 | 2023-12-18 | 2024-01-22 | 3 | 2.5 | 0.05 | 7 | 0.04 | 5.3 | 7.41 | 1 | 4.3 | 2.5
| 2023-12-21 | 2024-01-05 | 2024-01-22 | 1 | 19 | 0.02 | 5 | 0.07 | 8 | 7.8 | 2.3 | 5.67 | 2.5
| 2024-01-02 | 2024-01-10 | 2024-02-15 | 1 | 2.5 | 0.02 | 1 | 0.01 | 6.4 | 7.91 | 1.3 | 5.08 | 2.5
| 2024-01-12 | 2024-01-19 | 2024-02-15 | 8 | 2.5 | 0.02 | 20 | 0.03 | 7.6 | 7.51 | 1 | 6.65 | 2.5
| 2024-01-22 | 2024-01-30 | 2024-02-15 | 2 | 2.5 | 0.02 | 8 | 0.04 | 3.4 | 8.1 | 1.2 | 2.18 | 2.5
| 2024-02-05 | 2024-02-12 | 2024-03-15 | 3 | 2.5 | 0.05 | 82 | 0.03 | 1.8 | 7.81 | 1 | 0.83 | 2.5
| 2024-02-19 | 2024-02-27 | 2024-03-15 | 9 | 2.5 | 0.26 | 83 | 0.04 | 1 | 7.93 | 0.9 | 0.05 | 2.5
| 2024-03-04 | 2024-03-11 | 2024-04-16 | 13 | 2.5 | 0.05 | 30 | 0.005 | 1.2 | 7.51 | 0.8 | 0.36 | 2.5
| 2024-03-18 | 2024-03-25 | 2024-04-16 | 9 | 2.5 | 0.07 | 7 | 0.005 | 1.4 | 7.87 | 0.7 | 0.72 | 2.5
| 2024-03-28 | 2024-04-12 | 2024-04-16 | 4 | 2.5 | 0.22 | 0.5 | 0.02 | 2.3 | 7.85 | 1.1 | 1.19 | 2.5
| 2024-04-08 | 2024-04-16 | 2024-05-14 | 1 | 2.5 | 0.03 | 0.5 | 0.15 | 1 | 7.59 | 0.7 | 0.28 | 2.5
| 2024-04-22 | 2024-04-30 | 2024-05-14 | 3 | 2.5 | 0.39 | 0.5 | 0.08 | 1.5 | 8.02 | 1.1 | 0.36 | 2.5
| 2024-05-06 | 2024-05-14 | 2024-06-17 | 4 | 2.5 | 0.05 | 0.5 | 0.04 | 5.3 | 7.82 | 1.1 | 4.21 | 2.5
| 2024-05-20 | 2024-05-27 | 2024-06-17 | 5 | 34 | 0.04 | 0.5 | 0.14 | 1.4 | 7.47 | 1.1 | 0.29 | 2.5
| 2024-06-03 | 2024-06-12 | 2024-07-09 | 7 | 2.5 | 0.14 | 0.5 | 0.1 | 1.1 | 7.79 | 1.1 | 0.02 | 2.5
| 2024-06-17 | 2024-06-24 | 2024-07-09 | 6 | 2.5 | 0.22 | 0.5 | 0.04 | 1 | 7.63 | 0.9 | 0.05 | 2.5
Comments:
July 2023 - All data within license limits
Aug 2023 - All data within license limits
Sep 2023 - All data within license limits
October 2023 - All data within license limits
November 2023 - All data within license limits
December 2023 - All data within license limits
January 2024 - All data within license limits
February 2024 - All data within license limits
March 2024 - All data within license limits
April 2024 - All data within license limits
May 2024 - All data within license limits
June 2024 - All data within license limits
2024 / 2025 | 2024-07-01 | 2024-07-08 | 2024-08-19 | 4 | 6 | 0.04 | 0.5 | 0.03 | 0.6 | 7.54 | 0.5 | 0.08 | 2.5
| 2024-07-15 | 2024-07-22 | 2024-08-19 | 9 | 2.5 | 0.16 | 0.5 | 0.15 | 1.2 | 7.24 | 1 | 0.24 | 2.5
| 2024-07-29 | 2024-08-05 | 2024-08-19 | 11 | 2.5 | 0.03 | 0.5 | 0.02 | 0.9 | 6.87 | 0.8 | 0.06 | 2.5
| 2024-08-12 | 2024-08-20 | 2024-09-18 | 11 | 2.5 | 0.08 | 0.5 | 0.04 | 1.1 | 6.92 | 1 | 0.08 | 2.5
| 2024-08-27 | 2024-09-03 | 2024-09-18 | 8 | 2.5 | 0.08 | 0.5 | 0.005 | 1.3 | 7.66 | 1 | 0.26 | 2.5
| 2024-09-09 | 2024-09-16 | 2024-10-16 | 1 | 5 | 0.08 | 0.5 | 0.05 | 1.6 | 6.86 | 0.8 | 0.75 | 2.5
| 2024-09-23 | 2024-10-01 | 2024-10-16 | 1 | 6 | 0.11 | 0.5 | 0.16 | 1.4 | 7.26 | 0.9 | 0.49 | 0.5
| 2024-10-03 | 2024-10-14 | 2024-11-18 | 2 | 8 | 0.09 | 0.5 | 0.08 | 1.9 | 6.95 | 0.9 | 0.97 | 0.5
| 2024-10-14 | 2024-10-21 | 2024-11-18 | 1 | 10 | 0.07 | 0.5 | 0.11 | 1.4 | 7.28 | 0.8 | 0.56 | 0.5
| 2024-10-28 | 2024-11-05 | 2024-11-18 | 2 | 2.5 | 0.07 | 0.5 | 0.04 | 0.8 | 7.19 | 0.7 | 0.13 | 0.5
| 2024-11-11 | 2024-11-18 | 2024-12-12 | 1 | 2.5 | 0.1 | 0.5 | 0.06 | 0.8 | 7.27 | 0.7 | 0.15 | 0.5
| 2024-11-25 | 2024-12-02 | 2024-12-12 | 4 | 2.5 | 0.6 | 0.5 | 0.07 | 1.4 | 7.11 | 1.4 | 0.05 | 0.5
| 2024-12-09 | 2024-12-17 | 2025-01-15 | 1 | 14 | 0.06 | 6 | 0.11 | 0.8 | 7.32 | 0.6 | 0.21 | 2.5
| 2024-12-23 | 2025-01-06 | 2025-01-15 | 1 | 8 | 0.18 | 0.5 | 0.04 | 2.1 | 7.78 | 1.1 | 1 | 2.5
| 2025-01-06 | 2024-01-13 | 2025-02-20 | 1 | 2.5 | 0.08 | 0.5 | 0.005 | 0.9 | 7.85 | 0.8 | 0.13 | 2.5
| 2025-01-20 | 2025-01-28 | 2025-02-20 | 2 | 2.5 | 0.1 | 0.5 | 0.01 | 0.8 | 7.53 | 0.6 | 0.18 | 2.5
| 2025-02-03 | 2025-02-10 | 2025-03-13 | 3 | 8 | 0.13 | 0.5 | 0.05 | 1.3 | 7.96 | 1 | 0.26 | 2.5
| 2025-02-17 | 2025-02-24 | 2025-03-13 | 1 | 2.5 | 0.06 | 4 | 0.16 | 1.1 | 7.57 | 0.7 | 0.44 | 2.5
Comments:
July 2024 - All data within license limits
Aug 2024 - All data within license limits
Sep 2024 - All data within license limits
October 2024 - All data within license limits
November 2024 - All data within license limits
December 2024 -All data within license limits
January 2025 - All data within license limits
February 2025 -All data within license limits
March 2025 -
April 2025 -
May 2025 -
June 2025 -

## SWSTP Volume Data Final
H a w k e s b u r y C i t y C o u n c i l
366 George Street (PO Box 146) Windsor NSW 2756 DX 8601 WINDSOR
Phone: (02) 4560 4444 Facsimilie: (02) 4587 7740 Email:council@hawkesbury.nsw.gov.au
South Windsor Sewage Treatment Plant Monitoring Data
|  |  |  | EPA License number: |  | 3306 |  |  |  |  | Monitoring Point: |  | EPA 3, V-notch weir (discharge into South Creek)
|  |  |  | License website link: |  | http://app.epa.nsw.gov.au/prpoeoapp/ |  |  |  |  | Sampling Frequency: |  | Daily
[5 empty] | Licensee: | Hawkesbury City Council |  |  |  |  | Premises: | Fairey Road South Windsor NSW
|  |  |  | Data Publish Date: |  | 2025-03-13
Note: Uncontrolled document when printed
2019 / 2020 | 1 | 3.568 | 2.213 | 3.536 | 1.86 | 3.0158 | 3.48 | 2.606 | 1.789 | 1.539 | 1.314 | 2.626 | 3.467
| 2 | 3.324 | 2.493 | 1.071 | 3.181 | 3.031 | 5.26 | 2.006 | 2.063 | 1.719 | 2.744 | 2.881 | 3.33
| 3 | 3.756 | 3.059 | 0.021 | 2.413 | 3.5246 | 4.54 | 2.066 | 2.164 | 1.61 | 3.341 | 2.771 | 3.599
| 4 | 3.422 | 3.973 | 3.534 | 2.35 | 3.1723 | 7.48 | 3.118 | 1.888 | 1.322 | 3.002 | 1.6445 | 3.487
| 5 | 2.959 | 3.297 | 5.763 | 0.624 | 2.4466 | 6.26 | 3.032 | 1.894 | 1.474 | 2.604 | 1.832 | 1.915
| 6 | 3.48 | 3.123 | 5.05 | 0.446 | 2.7512 |  | 2.268 | 2.095 | 1.539 | 2.149 | 7.349 | 4.173
| 7 | 7.082 | 2.89 | 4.466 | 3.111 | 2.8224 | 3.17 | 2.47 | 1.993 | 2.236 | 6.945 | 7.336 | 2.508
| 8 | 0 | 2.044 | 4.281 | 4.1291 | 3.2723 | 2.81 | 2.441 | 1.974 | 1.876 | 6.168 | 6.507 | 3.787
| 9 | 3 | 2.529 | 4.571 | 4.2637 | 3.3095 | 2.35 | 2.512 | 2.453 | 1.937 | 3.691 | 3.592 | 4.036
| 10 | 2.556 | 3.201 | 4.028 | 3.8393 | 3.9916 | 3.8 | 2.32 | 2.494 | 1.815 | 4.207 | 3.874 | 3.1308
| 11 | 4.732 | 3.456 | 4.254 | 3.7813 | 3.8551 | 4.95 | 2.761 | 2.089 | 1.596 | 6.15 | 3.301 | 3.093
| 12 | 3.829 | 3.274 | 4.778 | 3.642 | 3.71 | 4.65 | 2.725 | 2.402 | 1.845 | 6.967 | 2.816 | 3.085
| 13 | 4.139 | 3.191 | 3.964 | 4.3937 | 3.2863 | 3.6 | 2.591 | 2.233 | 2.357 | 2.968 | 3.773 | 3.333
| 14 | 2.91 | 3.189 | 3.486 | 4.8397 | 3.1884 | 4.82 | 3.549 | 2.078 | 2.455 | 6.13 | 4.218 | 3.502
| 15 | 5.01 | 2.751 | 3.876 | 4.2366 | 3.2908 | 4.66 | 2.191 | 2.078 | 2.122 | 5.633 | 3.729 | 3.186
| 16 | 4.288 | 2.686 | 4.214 | 4.4253 | 3.1165 | 3.36 | 2.057 | 2.255 | 3.0096 | 5.406 | 3.852 | 2.97
| 17 | 4.269 | 3.351 | 3.786 | 2.8897 | 6.0249 | 3.08 | 1.988 | 2.615 | 2.664 | 5.284 | 4.215 | 3.224
| 18 | 4.126 | 3.329 | 3.285 | 3.0156 | 4.6042 | 3.61 | 3.476 | 1.899 | 1.963 | 4.302 | 3.726 | 3.759
| 19 | 3.789 | 3.178 | 3.055 | 2.9538 | 7.3886 | 3.2 | 2.222 | 1.949 | 2.378 | 1.495 | 3.28 | 2.752
| 20 | 3.738 | 3.696 | 2.3 | 4.6037 | 4.6493 | 2.9993 | 2.079 | 1.86 | 3.069 | 5.003 | 4.387 | 2.857
| 21 | 3.831 | 3.238 | 2.409 | 3.5642 | 3.8624 | 3.343 | 2 | 1.546 | 2.739 | 8.981 | 2.42 | 2.972
| 22 | 3.724 | 2.671 | 2.979 | 2.9625 | 3.2176 | 3.115 | 1.962 | 1.882 | 2.45 | 4.519 | 4.37 | 3.107
| 23 | 3.477 | 0.047 | 3.372 | 3.0637 | 3.8832 | 2.417 | 1.844 | 2.18 | 2.443 | 2.014 | 4.307 | 3.201
| 24 | 3.09 | 0.009 | 2.971 | 3.7958 | 4.3789 | 2.368 | 2.027 | 2.405 | 2.807 | 4.585 | 3.996 | 2.677
| 25 | 2.718 | 0.009 | 3.186 | 3.1479 | 3.9804 | 2.336 | 3.05 | 1.909 | 2.147 | 1.992 | 3.357 | 2.503
| 26 | 2.724 | 1.3 | 3.145 | 2.8381 | 3.36 | 1.966 | 2.811 | 1.748 | 2.018 | 2.757 | 3.868 | 2.488
| 27 | 3.73 | 3.516 | 0.644 | 3.9423 | 3.26 | 2.588 | 2.768 | 2.195 | 2.264 | 2.702 | 2.851 | 3.027
| 28 | 3.262 | 3.479 | 0.024 | 3.1145 | 2.86 | 3.29 | 2.568 | 1.577 | 2.175 | 3.051 | 2.301 | 3.15
| 29 | 2.911 | 3.256 | 2.083 | 3.7479 | 3.09 | 3.299 | 1.995 | 1.624 | 1.324 | 2.589 | 13.3 | 3.167
| 30 | 3.006 | 3.416 | 3.287 | 3.4913 | 3.38 | 2.539 | 1.912 | 2.102 | 1.255 |  | 3.924 | 4.266
| 31 | 2.939 |  | 3.068 |  |  | 2.794 |  | 2.1147 | 1.149 |  | 4.682
Reporting Year | Day Of Month | Volume Monitoring - Unit- megalitres per day
|  | 2020-07-01 | 2020-08-01 | 2020-09-01 | 2020-10-01 | 2020-11-01 | 2020-12-01 | 2021-01-01 | 2021-02-01 | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | Comments
2020 / 2021 | 1 | 3.092 | 4.093 | 2.958 | 1.766 | 4.665 | 2.469 | 2.778 | 1.541 | 2.626 | 3.257 | 3.314 | 4.077
| 2 | 2.263 | 2.826 | 2.5289 | 1.398 | 4.418 | 4.213 | 2.736 | 2.614 | 2.881 | 3.3655 | 3.071 | 3.654
| 3 | 2.63 | 1.318 | 2.4475 | 1.148 | 4.73 | 2.808 | 2.699 | 5.048 | 2.771 | 2.956 | 3.835 | 4.404
| 4 | 2.25 | 2.511 | 1.738 | 9.384 | 4.622 | 1.756 | 2.146 | 5.593 | 1.6445 | 2.524 | 4.574 | 3.776
| 5 | 3.527 | 7.263 | 1.0225 | 8.954 | 3.436 | 4.002 | 2.646 | 4.52 | 1.832 | 2.555 | 4.375 | 3.519
| 6 | 4.001 | 7.501 | 1.541 | 2.735 | 3.463 | 4.003 | 3.166 | 4.074 | 7.349 | 4.194 | 5.298 | 3.656
| 7 | 2.25 | 6.457 | 2.087 | 1.464 | 3.967 | 2.061 | 4.455 | 4.163 | 7.336 | 5.404 | 7 | 3.9
| 8 | 2.506 | 4.257 | 2.342 | 3.039 | 3.404 | 2.473 | 4.088 | 3.921 | 6.507 | 4.315 | 4.864 | 4.596
| 9 | 4.726 | 3.1158 | 3.349 | 2.954 | 3.932 | 4.023 | 3.305 | 3.995 | 3.592 | 3.899 | 3.704 | 5.041
| 10 | 4.141 | 8.595 | 2.77 | 2.773 | 3.718 | 4.144 | 2.723 | 3.944 | 3.874 | 3.178 | 3.842 | 5.871
| 11 | 3.842 | 4.28 | 2.153 | 2.892 | 3.803 | 3.708 | 3.136 | 3.86 | 3.301 | 3.203 | 4.272 | 5.061
| 12 | 4.164 | 5.002 | 1.182 | 2.858 | 4.052 | 3.714 | 2.931 | 3.64 | 2.816 | 8.99 | 3.851 | 4.018
| 13 | 3.992 | 5.724 | 1.2458 | 3.063 | 4.262 | 3.214 | 2.687 | 2.481 | 3.773 | 16.321 | 4.135 | 3.46
| 14 | 3.384 | 4.726 | 2.312 | 2.571 | 4.115 | 2.975 | 3.004 | 2.631 | 4.218 | 3.072 | 3.933 | 4.453
| 15 | 2.488 | 5.6345 | 1.7306 | 3.045 | 4.048 | 3.354 | 2.54 | 3.646 | 3.729 | 5.362 | 4.055 | 5.272
| 16 | 3.663 | 4.789 | 1.388 | 2.852 | 3.757 | 2.92 | 2.337 | 3.997 | 3.852 | 3.559 | 4.317 | 5.068
| 17 | 2.39 | 4.749 | 1.999 | 2.624 | 3.419 | 3.486 | 2.419 | 3.671 | 4.215 | 3.223 | 4.824 | 6.043
| 18 | 2.367 | 3.45 | 1.516 | 2.493 | 2.88 | 3.016 | 2.719 | 3.934 | 3.726 | 3.409 | 4.794 | 4.522
| 19 | 2.372 | 4.076 | 9 | 3.352 | 9.399 | 2.812 | 2.927 | 4.268 | 3.28 | 3.799 | 4.758 | 3.635
| 20 | 3.42 | 5.139 | 2.046 | 3.122 | 12.62 | 2.869 | 3.071 | 3.627 | 4.387 | 4.319 | 4.839 | 3.713
| 21 | 5.559 | 5.433 | 2.281 | 3.035 | 2.717 | 3.845 | 3.078 | 3.479 | 2.42 | 5.388 | 4.539 | 4.52
| 22 | 3.934 | 4.455 | 2.086 | 2.948 | 2.653 | 4.553 | 2.549 | 3.942 | 4.37 | 5.794 | 4.299 | 5.523
| 23 | 0.1935 | 4.402 | 1.854 | 2.884 | 2.85 | 3.54 | 1.867 | 4.28 | 4.307 | 4.413 | 4.17 | 5.145
| 24 | 1.038 | 5.205 | 2.112 | 3.849 | 2.285 | 3.239 | 1.889 | 4.099 | 3.996 | 4.036 | 3.461 | 5.522
| 25 | 4.331 | 5.912 | 1.958 | 4.403 | 2.737 | 2.229 | 2.543 | 3.647 | 3.357 | 3.746 | 4.165 | 4.704
| 26 | 2.048 | 4.556 | 1.779 | 3.976 | 0.736 | 2.7 | 2.359 | 3.453 | 3.868 | 3.357 | 3.871 | 3.432
| 27 | 6.491 | 4.953 | 1.825 | 5.014 | 1.071 | 2.399 | 2.73 | 2.448 | 2.851 | 3.731 | 4.769 | 3.904
| 28 | 8.598 | 2.867 | 2.281 | 3.725 | 2.29 | 3.334 | 1.068 | 2.574 | 2.301 | 3.813 | 4.991 | 4.232
| 29 | 5.632 | 2.776 | 2.868 | 5.234 | 2.279 | 4.98 | 7.189 |  | 13.3 | 4.215 | 4.902 | 5.33
| 30 | 4.447 | 2.823 | 1.517 | 4.784 | 1.554 | 5.017 | 1.632 |  | 3.924 | 4.128 | 3.348 | 5.07
| 31 | 2020-07-01: 4.066; 2020-08-01: 2.553; 2020-10-01: 4.852; 2020-12-01: 3.584; 2021-01-01: 1.502; 2021-03-01: 4.682; 2021-05-01: 4.281
Reporting Year | Day Of Month | 2020-07-01: Volume Monitoring - Unit- megalitres per day
|  | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 | 2022-01-01 | 2022-02-01 | 2022-03-01 | 2022-04-01 | 2022-05-01 | 2022-06-01 | Comments
2021 / 2022 | 1 | 4.589 | 3.301 | 3.524 | 3.575 | 3.559 | 4.485 | 2.279 | 3.53 | 7.653 | 7.432 | 4.749 | 5.078
| 2 | 4.586 | 4.481 | 4.569 | 3.864 | 4.85 | 4.274 | 2.22 | 5.614 | 19.075 | 5.819 | 4.872 | 6.088
| 3 | 4.863 | 4.196 | 4.217 | 3.3733 | 4.771 | 3.576 | 2.35 | 5.582 |  | 5.09 | 4.505 | 4.951 | 3 March 2022 - Data not recorded due power outage
| 4 | 4.736 | 4.381 | 3.897 | 2.776 | 4.475 | 4.823 | 2.949 | 4.188 | 8.063 | 5.104 | 4.726 | 4.576
| 5 | 5.7025 | 4.926 | 4.174 | 3.567 | 5.233 | 3.566 | 3.637 | 3.606 | 3.36 | 4.777 | 4.198 | 4.39
| 6 | 6.2083 | 4.759 | 5.051 | 3.309 | 4.526 | 3.878 | 5.511 | 2.967 | 7.485 | 5.075 | 4.611 | 4.499
| 7 | 5.7225 | 4.91 | 5.224 | 2.045 | 2.856 | 4.726 | 2.973 | 5.29 | 6.424 | 7.685 | 5.089 | 5.078
| 8 | 5.806 | 4.391 | 4.321 | 3.131 | 7.305 | 5.162 | 7.904 | 4.907 | 5.482 | 13.862 | 4.635 | 5.459
| 9 | 4.8775 | 3.806 | 4.559 | 3.568 | 4.923 | 7.675 | 3.258 | 4.027 | 6.537 | 8.796 | 4.82 | 6.472
| 10 | 4.2377 | 4.506 | 3.651 | 2.961 | 3.671 | 8.019 | 3.383 | 3.26 | 4.27 | 6.176 | 5.553 | 6.084
| 11 | 4.4332 | 4.279 | 3.772 | 4.108 | 2.455 | 4.994 | 3.634 | 4.209 | 3.746 | 4.915 | 6.103 | 5.166
| 12 | 5.405 | 3.416 | 3.174 | 4.594 | 4.287 | 3.656 | 3.461 | 3.483 | 3.612 | 4.745 | 7.673 | 3.973
| 13 | 5.328 | 4.786 | 3.443 | 4.697 | 5.713 | 4.102 | 9.899 | 3.755 | 4.345 | 4.382 | 7.864 | 5.444
| 14 | 4.808 | 4.512 | 4.659 | 1.689 | 2.846 | 3.768 | 3.9 | 4.101 | 4.464 | 6.177 | 5.054 | 5.983
| 15 | 4.295 | 4.354 | 4.485 | 1.942 | 4.239 | 3.868 | 3.396 | 4.514 | 4.659 | 4.984 | 4.145 | 6.142
| 16 | 4.168 | 4.169 | 4.6 | 4.376 | 2.892 | 3.326 | 2.905 | 4.179 | 4.844 | 3.831 | 4.656 | 5.085
| 17 | 3.846 | 4.361 | 4.378 | 3.38 | 5.065 | 3.325 | 3.304 | 3.762 | 3.167 | 3.056 | 4.683 | 4.89
| 18 | 4.112 | 4.94 | 3.459 | 3.093 | 4.649 | 2.819 | 4.022 | 4.086 | 5.772 | 3.287 | 5.276 | 4.538
| 19 | 5.305 | 4.616 | 3.498 | 4.078 | 3.922 | 3.877 | 7.412 | 3.262 | 5.401 | 3.55 | 5.263 | 4.075
| 20 | 5.223 | 4.279 | 3.93 | 4.52 | 3.23 | 3.74 | 7.512 | 2.842 | 6.553 | 4.679 | 5.381 | 4.306
| 21 | 4.4419 | 3.497 | 3.941 | 4.417 | 4.597 | 3.289 | 5.169 | 3.767 | 4.696 | 4.793 | 4.096 | 5.159
| 22 | 6.283 | 3.719 | 4.45 | 4.713 | 6.321 | 3.345 | 4.038 | 6.274 | 4.654 | 4.2227 | 4.314 | 5.278
| 23 | 4.765 | 3.264 | 4.294 | 3.972 | 5.188 | 3.917 | 3.38 | 9.084 | 5.013 | 4.25 | 5.747 | 5.748
| 24 | 3.95 | 1.87 | 3.781 | 3.424 | 4.928 | 3.401 | 4.256 | 6.563 | 4.848 | 3.405 | 4.922 | 5.257
| 25 | 3.658 | 4.313 | 3.41 | 3.303 | 5.226 | 2.442 | 4.444 | 9.457 | 4.667 | 4.032 | 4.975 | 4.539
| 26 | 4.441 | 5.794 | 3.48 | 2.906 | 10.321 | 2.244 | 3.187 | 11.227 | 6.508 | 4.629 | 4.731 | 4.879
| 27 | 4.561 | 5.182 | 4.254 | 2.777 | 10.785 | 2.58 | 4.279 | 7.893 | 6.32 | 5.356 | 4.671 | 4.728
| 28 | 4.172 | 5.655 | 4.489 | 4.591 | 6.681 | 3.78 | 4.49 | 6.479 | 5.246 | 6.11 | 4.091 | 5.1624
| 29 | 4.038 | 4.825 | 2.114 | 5.099 | 5.836 | 3.695 | 3.274 |  | 15.719 | 5.533 | 4.401 | 3.473
| 30 | 5.322 | 5.191 | 4.132 | 4.099 | 6.112 | 3.621 | 2.868 |  | 12.867 | 4.872 | 5.43 | 1.743
| 31 | 2021-07-01: 4.673; 2021-08-01: 5.16; 2021-10-01: 2.613; 2021-12-01: 2.825; 2022-01-01: 3.148; 2022-03-01: 8.345; 2022-05-01: 5.187
Reporting Year | Day Of Month | 2021-07-01: Volume Monitoring - Unit- megalitres per day
|  | 2022-07-01 | 2022-08-01 | 2022-09-01 | 2022-10-01 | 2022-11-01 | 2022-12-01 | 2023-01-01 | 2023-02-01 | 2023-03-01 | 2023-04-01 | 2023-05-01 | 2023-06-01 | Comments
2022 / 2023 | 1 | 2.335 | 4.244 | 4.739 | 5.377 | 3.142 | 3.044 | 1.329 | 3.687 | 3.418 | 3.927 | 5.645 | 2.951
| 2 | 2.246 | 5.695 | 4.195 |  | 3.599 | 3.49 | 1.912 | 3.588 | 3.367 | 3.841 | 5.533 | 2.915 | 3 October 2022 - Data not recorded due to communication failure
| 3 | 11.641 | 4.745 | 4.13 | 4.39 | 3.804 | 3.023 | 2.42 | 3.592 | 2.899 | 4.108 | 4.383 | 2.629
| 4 | 11.875 | 3.989 | 4.112 | 4.359 | 3.238 | 2.884 | 3.328 | 3.398 | 2.678 | 4.053 | 8.702 | 2.361
| 5 | 12.121 | 4.647 | 5.553 | 5.759 | 3.226 | 3.448 | 4.308 | 3.275 | 2.871 | 4.029 |  | 3.147 | 5 to 11 May 2023 - Data incorrectly recorded
| 6 | 9.643 | 4.211 | 5.425 | 11.362 | 3.45 | 3.448 | 4.139 | 3.746 | 3.387 | 3.939 |  | 3.251
| 7 | 21.76 | 3.932 | 4.86 | 6.83 | 3.623 | 3.309 | 3.149 | 3.617 | 3.192 | 3.678 |  | 3.132
| 8 | 10.097 | 4.769 | 4.495 | 7.079 | 3.623 | 3.547 | 3.067 | 3.144 | 3.497 | 3.057 |  | 3.34
| 9 | 7.646 | 4.918 | 4.08 | 15.892 | 3.416 | 3.253 | 4.035 | 3.736 | 3.145 | 3.426 |  | 3.126
| 10 | 7.771 | 4.758 | 3.64 | 8.337 | 4.803 | 2.782 | 3.559 | 3.847 | 3.18 | 3.934 |  | 2.391
| 11 | 8.036 | 4.957 | 3.648 | 6.327 | 3.642 | 3.134 | 3.066 | 2.617 | 2.997 | 5.532 |  | 2.038
| 12 | 7.608 | 4.188 | 5.03 | 5.41 | 2.73 | 2.648 | 3.031 | 2.908 | 2.558 | 3.181 | 2.153 | 2.831
| 13 | 7.499 | 4.205 | 5.25 | 5.061 | 2.453 | 3.22 | 3.084 | 3.154 | 3.329 | 4.095 | 2.728 | 3.769
| 14 | 5.342 | 4.211 | 5.185 | 2.699 | 6.873 | 4.19 | 2.9 | 3.216 | 3.27 | 4.027 | 2.39 | 2.264
| 15 | 5.996 | 4.427 | 7.218 | 3.85 | 4.009 | 3.317 | 2.671 | 3.458 | 3.303 | 3.354 | 3.257 | 3.309
| 16 | 5.958 | 4.675 | 6.312 | 3.418 | 4.132 | 3.423 | 3.161 | 3.589 | 3.391 | 2.91 | 2.363 | 3.144
| 17 | 4.838 | 5.02 | 3.884 | 4.032 | 3.861 | 2.923 | 2.984 | 3.309 | 3.276 | 4.574 | 3.227 | 2.535
| 18 | 3.812 | 4.899 | 3.687 | 3.918 | 3.524 | 2.829 | 3.4 | 2.638 | 2.824 | 4.185 | 3.123 | 2.47
| 19 | 5.575 | 4.361 | 4.882 | 3.692 | 3.183 | 3.332 | 4.574 | 2.899 | 2.52 | 4.014 | 3.061 | 3.061
| 20 | 5.471 | 4.817 | 5.317 | 3.287 | 2.565 | 4.566 | 3.802 | 3.363 | 3.422 | 4.013 | 2.793 | 3.013
| 21 | 5.128 | 3.554 | 5.019 | 3.414 | 3.523 | 3.394 | 2.995 | 3.136 | 3.636 | 3.846 | 2.759 | 3.001
| 22 | 5.398 | 4.499 | 4.707 | 3.259 | 3.725 | 3.522 | 3.812 | 6.897 | 3.782 | 3.642 | 3.181 | 3.414
| 23 | 4.663 | 4.377 | 5.151 | 3.45 | 3.595 | 3.017 | 4.088 | 5.971 | 3.616 | 3.304 | 2.957 | 3.455
| 24 | 4.655 | 6.272 | 10.826 | 4.705 | 2.911 | 2.25 | 3.851 | 5.196 | 3.207 | 3.567 | 3.334 | 2.868
| 25 | 4.65 | 5.177 | 5.777 | 4.709 | 2.899 | 2.232 | 3.598 | 4.506 | 3.331 | 3.444 | 3.059 | 2.588
| 26 | 5.394 | 4.31 | 5.751 | 4.494 | 3.157 | 3.019 | 2.834 | 3.397 | 2.987 | 4.078 | 3.071 | 3.195
| 27 | 6.054 | 3.981 | 5.844 | 4.126 | 3.075 | 3.127 | 3.05 | 3.478 | 4.597 | 4.07 | 2.728 | 3.277
| 28 | 5.738 | 3.743 | 7.539 | 3.672 | 4.06 | 2.644 | 2.582 | 3.509 | 4.767 | 3.829 | 2.67 | 3.421
| 29 | 5.053 | 3.904 | 6.326 | 3.986 | 3.554 | 2.429 | 2.923 |  | 4.439 | 4.965 | 2.726 | 3.291
| 30 | 5.76 | 3.735 | 5.908 | 3.86 | 3.311 | 1.815 | 4.22 |  | 4.504 | 7.501 | 3.403 | 2.778
| 31 | 2022-07-01: 5.118; 2022-08-01: 4.505; 2022-10-01: 3.86; 2022-12-01: 1.784; 2023-01-01: 5.21; 2023-03-01: 3.927; 2023-05-01: 3.256
Reporting Year | Day Of Month | 2022-07-01: Volume Monitoring - Unit- megalitres per day
|  | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | Comments
2023 / 2024 | 1 | 2.712 | 3.034 | 3.216 | 1.938 | 2.939 | 3.11 | 2.176 | 2.999 | 3.066 | 2.821 | 3.58 | 4.556
| 2 | 2.66 | 2.851 | 2.414 | 1.614 | 2.778 | 2.576 | 2.882 | 2.504 | 2.614 | 3.141 | 3.51 | 6.777
| 3 | 3.522 | 3.022 | 2.23 | 2.765 | 2.741 | 2.841 | 2.843 | 2.481 | 2.734 | 3.198 | 3.633 | 4.603
| 4 | 3.269 | 2.637 | 3.038 | 3.219 | 2.199 | 3.163 | 3.572 | 2.349 | 2.972 | 3.993 | 3.228 | 4.299
| 5 | 3.268 | 2.205 | 2.866 | 2.537 | 3.527 | 2.924 | 3.03 | 3.185 | 3.164 | 11.433 | 3.615 | 4.018
| 6 | 3.282 | 2.495 | 3.088 | 3.187 | 3.111 | 2.972 | 2.731 | 6.246 | 2.958 | 22.779 | 6.798 | 5.581
| 7 | 3.102 | 2.915 | 2.832 | 2.363 | 2.739 | 3.075 | 2.613 | 3.983 | 3.236 | 5.668 | 4.13 | 8.441
| 8 | 2.915 | 3.014 | 2.542 | 2.494 | 2.932 | 2.856 | 3.527 | 3.473 | 2.766 | 5.641 | 4.336 | 4.732
| 9 | 2.786 | 3.071 | 2.427 | 2.829 | 3.022 | 2.233 | 3.329 | 4.131 | 2.603 | 12.042 | 4.371 | 3.498
| 10 | 2.854 | 2.666 | 2.319 | 2.853 | 2.769 | 2.332 | 3.121 | 3.54 | 2.534 | 5.421 | 4.275 | 3.716
| 11 | 3.248 | 3.072 | 3.627 | 2.481 | 2.092 | 3.283 | 3.151 | 3.297 | 3.127 | 4.502 | 6.457 | 3.908
| 12 | 3.067 | 2.646 | 3.001 | 2.862 | 3.105 | 2.847 | 3.636 | 2.753 | 3.208 | 4.594 | 3.813 | 3.698
| 13 | 3.091 | 2.68 | 3.194 | 2.796 | 2.411 | 2.911 | 2.425 | 3.613 | 2.979 | 3.901 | 4.133 | 3.618
| 14 | 2.76 | 4.143 | 3.029 | 1.908 | 2.806 | 3.181 | 3.778 | 3.21 | 2.88 | 3.905 | 3.822 | 3.561
| 15 | 2.719 | 3.613 | 2.609 | 1.782 | 2.85 | 2.822 | 9.946 | 3.374 | 3.442 | 3.869 | 3.781 | 3.638
| 16 | 2.57 | 3.115 | 2.937 | 2.951 | 2.83 | 2.436 | 6.914 | 3.402 | 2.422 | 4.145 | 3.751 | 3.611
| 17 | 3.229 | 3.007 | 2.805 | 2.866 | 2.522 | 2.085 | 6.763 | 3.651 | 3.003 | 3.789 | 3.277 | 3.882
| 18 | 2.985 | 3.728 | 2.0007 | 2.793 | 2.388 | 2.746 | 7.329 | 3.133 | 3.252 | 3.706 | 3.384 | 3.702
| 19 | 3.299 | 2.574 | 3.289 | 2.898 | 2.87 | 2.926 | 4.801 | 4.736 | 3.258 | 3.637 | 2.988 | 3.744
| 20 | 3.282 | 2.869 | 2.063 | 2.687 | 2.133 | 6.591 | 4.03 | 5.151 | 3 | 2.887 | 3.654 | 3.501
| 21 | 3.114 | 3.041 | 3.16 | 2.521 | 2.66 | 2.047 | 3.668 | 4.114 | 2.415 | 3.059 | 3.708 | 3.161
| 22 | 2.596 | 3.322 | 2.64 | 2.542 | 2.664 | 3.227 | 4.784 | 3.972 | 2.838 | 3.628 | 3.245 | 6.127
| 23 | 2.433 | 2.847 | 2.215 | 2.81 | 2.481 | 2.588 | 4.73 | 3.746 | 2.488 | 3.898 | 3.321 | 3.194
| 24 | 3.306 | 2.982 | 2.283 | 2.611 | 2.403 | 2.675 | 4.594 | 3.662 | 2.666 | 3.588 | 3.228 | 3.646
| 25 | 3.14 | 2.857 | 2.898 | 2.748 | 2.562 | 2.315 | 4.382 | 3.499 | 2.744 | 3.35 | 2.743 | 4.115
| 26 | 3.356 | 2.548 | 2.91 | 2.725 | 2.249 | 2.469 | 3.493 | 3.598 | 3.367 | 2.913 | 2.899 | 3.291
| 27 | 3.323 | 2.526 | 2.668 | 3.494 | 3.205 | 3.986 | 6.962 | 3.785 | 3.109 | 2.839 | 3.362 | 3.696
| 28 | 2.478 | 3.056 | 3.074 | 2.988 | 2.979 | 3.072 | 3.698 | 3.616 | 2.602 | 2.842 | 3.279 | 4.156
| 29 | 2.308 | 3.133 | 2.95 | 1.009 | 4.133 | 2.957 | 4.148 | 3.233 | 2.522 | 3.49 | 3.619 | 2.353
| 30 | 2.49 | 3.125 | 2.028 | 2.41 | 3.324 | 2.245 | 3.96 |  | 2.356 | 3.659 | 3.35 | 5.34
| 31 | 2023-07-01: 3.011; 2023-08-01: 3.157; 2023-10-01: 2.633; 2023-12-01: 2.267; 2024-01-01: 3.276; 2024-03-01: 2.1; 2024-05-01: 3.232
Reporting Year | Day Of Month | 2023-07-01: Volume Monitoring - Unit- megalitres per day
|  | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01 | Comments
2024 / 2025 | 1 | 4.16 | 3.549 | 2.223 | 3.341 | 2.618 | 2.931 | 3.349 | 2.651
| 2 | 4.093 | 3.214 | 3.119 | 2.931 | 2.486 | 2.415 | 3.69 | 2.129
| 3 | 4.009 | 2.891 | 3.078 | 3.293 | 3.157 | 2.98 | 3.114 | 2.345
| 4 | 3.482 | 3.527 | 3.018 | 3.089 | 3.21 | 3.372 | 2.791 | 3.405
| 5 | 3.903 | 3.513 | 3.219 | 2.629 | 3.193 | 2.512 | 3.021 | 3.24
| 6 | 3.203 | 3.523 | 2.847 | 2.629 | 3.255 | 2.678 | 4.083 | 2.613
| 7 | 3.279 | 3.164 | 2.595 | 2.063 | 3.066 | 2.791 | 5.706 | 2.892
| 8 | 3.749 | 3.141 | 2.593 | 2.118 | 3.172 | 3.584 | 4.438 | 2.663
| 9 | 4.294 | 2.911 | 3.478 | 2.825 | 2.877 | 2.987 | 4.422 | 3.205
| 10 | 3.94 | 2.731 | 3.174 | 2.826 | 2.003 | 3.614 | 4.569 | 4.125
| 11 | 3.603 | 2.657 | 2.912 | 2.743 | 2.06 | 3.509 | 4.996 | 5.429
| 12 | 3.456 | 3.1 | 3.504 | 2.414 | 3.332 | 3.053 | 3.989 | 4.774
| 13 | 3.589 | 3.344 | 2.546 | 2.368 | 3.157 | 2.9 | 4.136 | 3.687
| 14 | 2.453 | 3.471 | 2.768 | 2.547 | 2.592 | 2.794 | 3.986 | 3.451
| 15 | 2024-07-01: 3.293; 2024-08-01: 3.62; 2024-09-01: 2.718; 2024-10-01: 3.178; 2024-11-01: 2.931; 2024-12-01: 2.711; 2025-02-01: 3.446 | 15/1/2025 -Data not recorded due to power outage
| 16 | 3.77 | 3.347 | 3.082 | 3.241 | 3.034 | 2.608 | 6.647 | 2.757
| 17 | 3.129 | 2.842 | 3.023 | 3.072 | 2.315 | 3.354 | 4.055 | 2.665
| 18 | 3.497 | 2.813 | 2.671 | 3.026 | 2.939 | 3.389 | 4.151 | 3.114
| 19 | 3.003 | 3.355 | 2.74 | 2.926 | 4.009 | 3.096 | 4.416 | 3.448
| 20 | 2.536 | 3.379 | 2.995 | 2.61 | 3.03 | 3.097 | 6.23 | 2.396
| 21 | 2.749 | 2.854 | 2.511 | 2.772 | 1.609 | 2.62 | 6.082 | 2.63
| 22 | 3.103 | 2.749 | 2.607 | 3.103 | 3.154 | 2.226 | 5.024 | 3.007
| 23 | 3.077 | 3.007 | 2.922 | 3.279 | 3.185 | 2.341 | 4.393 | 2.761
| 24 | 3.019 | 2.361 | 3.317 | 3.322 | 2.665 | 2.948 | 4.276 | 2.628
| 25 | 3.131 | 2.574 | 2.32 | 2.242 | 2.411 | 2.818 | 3.645 | 3.094
| 26 | 3.561 | 3.063 | 4.385 | 3.404 | 3.245 | 1.99 | 2.929 | 3.148
| 27 | 3.737 | 3.204 | 3.828 | 1.726 | 3.119 | 2.141 | 3.255 | 2.795
| 28 | 3.1 | 3.064 | 2.843 | 2.497 | 3.031 | 2.185 | 4.368 | 2.93
| 29 | 2024-07-01: 3.446; 2024-08-01: 3.507; 2024-09-01: 2.794; 2024-10-01: 3.479; 2024-11-01: 3.217; 2024-12-01: 2.06; 2025-01-01: 4.393
| 30 | 2024-07-01: 3.305; 2024-08-01: 2.735; 2024-09-01: 3.852; 2024-10-01: 2.521; 2024-11-01: 3.172; 2024-12-01: 1.873; 2025-01-01: 3.571
| 31 | 2024-07-01: 3.19; 2024-08-01: 2.374; 2024-10-01: 3.437; 2024-12-01: 2.701; 2025-01-01: 3.413

## SWSTP Volume Data Recycle
H a w k e s b u r y C i t y C o u n c i l
366 George Street (PO Box 146) Windsor NSW 2756 DX 8601 WINDSOR
Phone: (02) 4560 4444 Facsimilie: (02) 4587 7740 Email:council@hawkesbury.nsw.gov.au
South Windsor Sewage Treatment Plant Monitoring Data
|  |  |  | EPA License number: |  | 3306 |  |  |  |  | Monitoring Point: |  | EPA 5, Flow meter on recycled water system
|  |  |  | License website link: |  | http://app.epa.nsw.gov.au/prpoeoapp/ |  |  |  |  | Sampling Frequency: |  | Daily
[5 empty] | Licensee: | Hawkesbury City Council |  |  |  |  | Premises: | Fairey Road South Windsor NSW
|  |  |  | Data Publish Date: |  | 2025-03-13
Note: Uncontrolled document when printed
2019 / 2020 | 1 | 47.0391 | 626.734 | 149.82 | 1078.23 | 1116.03 | 732.81 | 1192.53 | 1025.34 | 1039.7 | 153.313 | 171.063 | 226.844
| 2 | 47.9766 | 631.688 | 134.344 | 1179.86 | 1034 | 721 | 1105.7 | 946.156 | 1230.61 | 196.281 | 125.25 | 258.938
| 3 | 66.4219 | 507.711 | 95.953 | 1178.5 | 1282.39 | 733.5 | 1056.77 | 1130.17 | 1105.09 | 190.75 | 319.219 | 258.063
| 4 | 69.2422 | 105.609 | 88.5234 | 1176.72 | 1247.03 | 793.03 | 969.67 | 1313.52 | 922.969 | 162.531 | 327.938 | 225.531
| 5 | 26.7031 | 46.8438 | 72.5 | 1145.87 | 1281.94 | 344.25 | 853.094 | 979.84 | 1016.5 | 220.531 | 320.594 | 226.813
| 6 | 175.195 | 107.414 | 45.3828 | 884.172 | 704.969 |  | 920.4 | 657.56 | 921 | 195.28 | 296.781 | 227.5
| 7 | 68.4219 | 89.664 | 28.4844 | 987.047 | 581.219 | 433.55 | 1089.97 | 538.53 | 604.172 | 190.938 | 192.781 | 256.594
| 8 | 62.8125 | 111.297 | 152.93 | 750.992 | 484.313 | 855.11 | 1108.7 | 607.078 | 980.563 | 162.469 | 35.1875 | 259.094
| 9 | 25.5469 | 152.125 | 123.336 | 727.188 | 846.625 | 1065.41 | 952.56 | 365.781 | 286.969 | 190.125 | 178.438 | 259.5
| 10 | 34.7422 | 115.133 | 188.953 | 655.898 | 924.766 | 1059.52 | 1146.75 | 298.5 | 278.781 | 191.313 | 232.969 | 226.938
| 11 | 86.0859 | 84.4844 | 312.445 | 802 | 994.938 | 1042.94 | 1089.81 | 634.484 | 255.156 | 520.906 | 327.531 | 225.625
| 12 | 89.1563 | 71.5547 | 174.031 | 575.063 | 979.531 | 915.67 | 1101.84 | 613.953 | 194.844 | 455.281 | 292.125 | 227.344
| 13 | 171.156 | 66.2422 | 136.477 | 825.969 | 915.984 | 947.25 | 1111.42 | 746.23 | 231.188 | 317.219 | 311.625 | 227.125
| 14 | 126.914 | 175.18 | 172.484 | 808.813 | 993.625 | 873.18 | 1121.75 | 664.063 | 197.375 | 314.563 | 294.5 | 208.875
| 15 | 28.5547 | 67.9453 | 253.852 | 753.672 | 519.078 | 1018.58 | 872.25 | 623.25 | 260.313 | 287.375 | 288.594 | 286.969
| 16 | 22.3047 | 69.7109 | 329.711 | 1033.95 | 186.719 | 1017.63 | 943.938 | 694.203 | 197.188 | 305.094 | 320.156 | 346.656
| 17 | 134.078 | 94.3672 | 195.531 | 1066.28 | 616.781 | 1063.98 | 1074 | 666.5 | 191.844 | 287.719 | 290 | 202.219
| 18 | 31.7188 | 67.5391 | 207.359 | 1107.83 | 876.297 | 1008.72 | 1032.75 | 926.016 | 166.188 | 284.563 | 327.188 | 224.5
| 19 | 144.852 | 76.3594 | 175.273 | 494.781 | 823.172 | 1061.56 | 814.78 | 1009.22 | 191.438 | 282.344 | 322.594 | 228.188
| 20 | 131.086 | 67.0859 | 156.297 | 256.047 | 724.281 | 1118.34 | 1496.44 | 1129.72 | 192.625 | 429.563 | 293.313 | 231.875
| 21 | 75.7422 | 127.469 | 162.68 | 243.797 | 661.813 | 1074.89 | 1488.8 | 582.797 | 165.219 | 224.969 | 296.031 | 231.219
| 22 | 50.3047 | 89.0703 | 460.445 | 329.359 | 660.813 | 1175.38 | 1235.27 | 621.047 | 226.531 | 245.969 | 325.781 | 266.688
| 23 | 61.1875 | 43.8672 | 524.227 | 768.875 | 705.969 | 1170.53 | 1055.91 | 826.9 | 225.719 | 5.375 | 291.469 | 233.406
| 24 | 94.1563 | 130.039 | 287.008 | 973.172 | 728.016 | 1384.13 | 1003.09 | 649.156 | 192.469 | 3.593 | 321.938 | 232.954
| 25 | 65.2578 | 100.031 | 346.266 | 909.203 | 783.844 | 1267.22 | 678.359 | 280.156 | 165 | 114.875 | 326.438 | 236.219
| 26 | 137.148 | 134.984 | 652.891 | 953.891 | 411.88 | 1209.8 | 632.063 | 335.375 | 191.563 | 288.813 | 292.875 | 230.219
| 27 | 347.766 | 223.172 | 815.547 | 1041.94 | 465.84 | 1116.13 | 908.656 | 666.531 | 192.313 | 349.125 | 303.219 | 231.813
| 28 | 652.75 | 194.055 | 357.156 | 1022.83 | 667.56 | 1169.09 | 955.953 | 875.203 | 193.5 | 289.469 | 279.5 | 231.406
| 29 | 670.336 | 65.3359 | 447.359 | 924.953 | 682.97 | 1088.09 | 1035.41 | 907.094 | 256.719 | 313.656 | 168.625 | 251.156
| 30 | 662.273 | 52.2891 | 755.633 | 523.797 | 590.56 | 1102.41 | 854.031 | 863.016 | 195.938 |  | 118.094 | 238.813
| 31 | 642.672 |  | 935.547 | 877.5 |  | 1052.36 |  | 831.875 | 195.84 |  | 197.188
Reporting Year | Day Of Month | Volume Monitoring - Unit- kilolitres per day
|  | 2020-07-01 | 2020-08-01 | 2020-09-01 | 2020-10-01 | 2020-11-01 | 2020-12-01 | 2021-01-01 | 2021-02-01 | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | Comments
2020 / 2021 | 1 | 595.813 | 544.344 | 821.938 | 845.438 | 888.688 | 1072.41 | 1016.81 | 680.75 | 771.938
| 2 | 675.219 | 495.406 | 790.594 | 844.969 | 854.469 | 873.594 | 1050.25 | 714.219 | 811.34 |  |  |  | 1-9 June 2021 - Flow meter affeted by the recent major wet weather event - under repair
| 3 | 1198.66 | 500.188 | 724.406 | 847.063 | 857.594 | 878 | 1055.75 | 748.625 | 759.813
| 4 | 1274.78 | 409.719 | 586.563 | 1146.5 | 881.906 | 927.688 | 1020.91 | 776.813 | 755.563
| 5 | 1279.97 | 464.188 | 550.938 | 843.281 | 893.594 | 959.219 | 1076.34 | 765.906 | 697.719
| 6 | 1304.78 | 508.906 | 512.469 | 786.125 | 848.219 | 959.875 | 1003.97 | 758.875 | 821.5
| 7 | 1396.5 | 468.031 | 554.281 | 781.031 | 945.844 | 954.938 | 970.781 | 761.031 | 768.813
| 8 | 1453.03 | 485.469 | 634.313 | 814.875 | 944.188 | 988.375 | 932.563 | 760.625 | 804.531
| 9 | 1299.22 | 480.688 | 605.594 | 783.813 | 775.313 | 1164.69 | 941.188 | 768.031 | 817.781
| 10 | 1082.38 | 478.219 | 763.594 | 813.594 | 933.563 | 1205.16 | 947.5 | 756.063 | 800.375 |  |  | 769.869
| 11 | 1059.97 | 570.625 | 793.844 | 780.156 | 904.781 | 1190.16 | 920.594 | 851.625 | 537.688 |  |  | 755.099
| 12 | 956.063 | 530.625 | 770.125 | 792.813 | 967.781 | 1127.84 | 915.406 | 834.219 |  |  |  | 717.927 | 12 - 31 March 2021 - Flow meter under repair
| 13 | 825.188 | 605.406 | 772.156 | 843.063 | 899.906 | 1135.34 | 920.563 | 831.75 |  |  |  | 743.249 | 1-30 April 2021 - Flow meter under repair
| 14 | 963.781 | 527.063 | 771.78 | 836.75 | 893.031 | 1138.28 | 939.719 | 852.344 |  |  |  | 745.993 | 1-31 May 2021 - Flow meter under repair
| 15 | 1126.59 | 595.531 | 644.219 | 867.531 | 879 | 1095.75 | 826.906 | 814 |  |  |  | 747.97
| 16 | 1094.47 | 530.375 | 409.938 | 841.813 | 967 | 971.813 | 609.969 | 821.844 |  |  |  | 785.684
| 17 | 863.219 | 533.375 | 561.063 | 829.563 | 980.875 | 1027.44 | 833.75 | 760.406 |  |  |  | 779.026
| 18 | 755.781 | 576.031 | 404.031 | 837 | 891.563 | 1006.63 | 872.844 | 804.125 |  |  |  | 769.068
| 19 | 774.281 | 360.969 | 286.63 | 807.469 | 991.5 | 978.656 | 810.281 | 755.094 |  |  |  | 716.005
| 20 | 768.406 | 552.531 | 408.469 | 783.375 | 919.875 | 985.969 | 769.625 | 755.469 |  |  |  | 746.958
| 21 | 849.781 | 826.219 | 544.063 | 768.813 | 889.563 | 1001.16 | 840.5 | 815.563 |  |  |  | 747.317
| 22 | 856.188 | 766.719 | 711.875 | 790.469 | 877.563 | 937.594 | 824.719 | 776.1 |  |  |  | 723.733
| 23 | 983.156 | 745.469 | 759.719 | 700.594 | 884.219 | 888.906 | 740.875 | 792.875 |  |  |  | 727.438
| 24 | 581.969 | 779.844 | 607.313 | 586.5 | 964.594 | 984.281 | 805.938 | 757.031 |  |  |  | 654.232
| 25 | 627.906 | 932.438 | 353.75 | 572.063 | 956.938 | 899.563 | 844.906 | 758.781 |  |  |  | 401.337
| 26 | 591.094 | 911.031 | 746.813 | 705.438 | 964.906 | 978.469 | 767.156 | 794.406 |  |  |  | 400.737
| 27 | 635.031 | 855.906 | 817.375 | 835.594 | 1045.25 | 1026.44 | 788.156 | 777.188 |  |  |  | 413.743
| 28 | 463.094 | 786.219 | 935.563 | 845.281 | 1263.28 | 1050.06 | 798.313 | 764.063 |  |  |  | 467.229
| 29 | 542.156 | 815.313 | 927.625 | 834.531 | 1219.94 | 1084.41 | 673.781 |  |  |  |  | 556.866
| 30 | 520.813 | 801.813 | 899.875 | 851.781 | 1074.69 | 1013.41 | 661.531 |  |  |  |  | 646.044
| 31 | 2020-07-01: 508.125; 2020-08-01: 781.688; 2020-10-01: 879.344; 2020-12-01: 1050.9; 2021-01-01: 677.781
Reporting Year | Day Of Month | 2020-07-01: Volume Monitoring - Unit- kilolitres per day
|  | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 | 2022-01-01 | 2022-02-01 | 2022-03-01 | 2022-04-01 | 2022-05-01 | 2022-06-01 | Comments
2021 / 2022 | 1 | 650.094 | 438.895 | 454.828 | 564.352 | 991.305 | 739.461 | 982.063 | 963.922 | 786.766 | 711.547 | 784.719 | 728.156
| 2 | 684.438 | 474.402 | 459.762 | 562.398 | 1061.94 | 727.516 | 907.031 | 980 | 810.016 | 699.438 | 802.328 | 674.063
| 3 | 630.666 | 445.824 | 496.066 | 746.262 | 1046.29 | 573.688 | 897.109 | 942.078 |  | 704 | 847.203 | 666.906 | 3 March 2022 - Data not recorded due power outage
| 4 | 657.467 | 413.672 | 450.609 | 764.625 | 842.32 | 700.461 | 917.078 | 968.094 | 329.344 | 708.156 | 861.047 | 615.063
| 5 | 674.643 | 537.25 | 445.762 | 740.125 | 879.586 | 713.102 | 952.594 | 949.25 | 792.094 | 745.031 | 844.656 | 618.531
| 6 | 650.016 | 728.25 | 461.918 | 780.492 | 741.969 | 770.234 | 959.938 | 945.172 | 788.688 | 795.516 | 809.844 | 631.969
| 7 | 595.029 | 667.004 | 455.719 | 1024.96 | 726.203 | 748.008 | 992.078 | 1010.2 | 790.313 | 778.938 | 752.766 | 642.281
| 8 | 651.236 | 642.977 | 536.914 | 1009.31 | 713.805 | 728.969 | 961.531 | 882.734 | 782.891 | 708.547 | 749.875 | 661.406
| 9 | 695.775 | 700.57 | 516.254 | 873.102 | 723.086 | 761.289 | 952.391 | 974.188 | 782.859 | 697.5 | 782.109 | 795.625
| 10 | 651.531 | 719.238 | 491.969 | 756.797 | 871.563 | 791.008 | 967.828 | 1006.77 | 783.953 | 692.266 | 746.063 | 754.094
| 11 | 683.46 | 624.316 | 310.301 | 890.625 | 685.992 | 699.578 | 976.719 | 1055.38 | 784.734 | 769.125 | 830.047 | 743.719
| 12 | 638.35 | 500.824 | 458.297 | 806.852 | 820.422 | 714.992 | 968.234 | 843.344 | 783.688 | 849.219 | 905.359 | 745.281
| 13 | 516.197 | 648.23 | 474.422 | 725.273 | 731.867 | 758.961 | 922.047 | 906.875 | 782.219 | 814.094 | 882.328 | 760.719
| 14 | 585.906 | 670.605 | 454.91 | 799.625 | 754.813 | 769.773 | 908.844 | 872.234 | 797.609 | 791.703 | 863.109 | 765.219
| 15 | 469.236 | 556.418 | 425.543 | 816.5 | 764.32 | 830.711 | 919.625 | 917.484 | 807.281 | 794.281 | 833.656 | 759.406
| 16 | 501.807 | 647.039 | 487.758 | 674.352 | 761.117 | 799.344 | 855.313 | 1006.28 | 831.203 | 785.594 | 841.641 | 776.219
| 17 | 591.385 | 745.23 | 519.09 | 671.391 | 812.602 | 828.5 | 889.844 | 942.75 | 872.906 | 806.563 | 849.766 | 735.438
| 18 | 600.609 | 741.051 | 513.84 | 842.586 | 987.313 | 777.602 | 850.297 | 984.984 | 797.266 | 800.031 | 890.984 | 745.469
| 19 | 620.346 | 698.984 | 520.883 | 835.508 | 1008.44 | 764.563 | 879.031 | 892.141 | 789.063 | 838.531 | 880.313 | 751.125
| 20 | 595.145 | 718.746 | 520.965 | 720.57 | 745.141 | 689.5 | 857.875 | 924.594 | 814.813 | 833.391 | 896.14 | 787.469
| 21 | 636.75 | 680.949 | 580.68 | 830.742 | 798.352 | 874.461 | 855.156 | 926.672 | 783.313 | 791.406 | 919.625 | 795.875
| 22 | 625.359 | 624.574 | 574.406 | 869.789 | 800.508 | 994.391 | 834.203 | 887.859 | 707.875 | 775.016 | 905.953 | 738.5
| 23 | 625.09 | 630.477 | 350.922 | 812.938 | 759.656 | 924.203 | 891.891 | 1021.31 | 652.172 | 785.781 | 890.297 | 781.313
| 24 | 621.078 | 630.477 | 691.469 | 676.555 | 761.578 | 400.281 | 1041.95 | 896.5 | 702.906 | 793.078 | 898.75 | 726.438
| 25 | 624.584 | 587.73 | 392.18 | 902.703 | 740.016 | 873.141 | 955.406 | 728.969 | 725.563 | 793.234 | 882.594 | 732.5
| 26 | 595.294 | 437.512 | 382.723 | 929.438 | 741.75 | 884.828 | 1016.2 | 828.016 | 697.203 | 814.938 | 933.375 | 733.75
| 27 | 544.15 | 408.59 | 548.172 | 792.883 | 722.938 | 912.344 | 1010.89 | 814.734 | 727.563 | 860.422 | 969 | 759.063
| 28 | 460.615 | 416.676 | 539.813 | 866.453 | 700.25 | 873.031 | 991.563 | 811.984 | 737.359 | 848.266 | 978.75 | 766.031
| 29 | 566.047 | 415.38 | 540.574 | 1074.34 | 759.094 | 918.844 | 980.484 |  | 719.234 | 580.281 | 911.625 | 728.875
| 30 | 574.176 | 414.582 | 504.656 | 1022.85 | 729.445 | 938.891 | 955.516 |  | 714.5 | 818.766 | 863.938 | 775.531
| 31 | 2021-07-01: 511.625; 2021-08-01: 484.344; 2021-10-01: 1028.72; 2021-12-01: 948.344; 2022-01-01: 982.594; 2022-03-01: 725.375; 2022-05-01: 847.469
Reporting Year | Day Of Month | 2021-07-01: Volume Monitoring - Unit- kilolitres per day
|  | 2022-07-01 | 2022-08-01 | 2022-09-01 | 2022-10-01 | 2022-11-01 | 2022-12-01 | 2023-01-01 | 2023-02-01 | 2023-03-01 | 2023-04-01 | 2023-05-01 | 2023-06-01 | Comments
2022 / 2023 | 1 | 404.531 | 811.188 | 815.438 | 1153.75 | 916.688 | 913 | 818.531 | 668.844 | 660.375 | 624.875 | 671.406 | 640.188
| 2 | 723.281 | 770.313 | 897 |  | 1007.31 | 917.688 | 808.094 | 656.938 | 645.281 | 601.688 | 657.938 | 573.75 | 2 October 2022 - Data not recorded due to communication failure
| 3 | 753.25 | 766.844 | 890 | 1115.47 | 1067.19 | 741.875 | 899.375 | 643.156 | 638.938 | 633.969 | 627.156 | 616.563
| 4 | 757.469 | 823.688 | 875.656 | 1117.47 | 1107.81 | 166.063 | 869.188 | 613.75 | 615.219 | 643.594 | 643.469 | 643.25
| 5 | 748 | 841.844 | 945.031 | 1044.13 | 1095.88 | 493.813 | 826.688 | 726.938 | 606.25 | 632.969 | 710.188 | 726.625
| 6 | 501.375 | 794.781 | 950.313 | 1067.53 | 1065.25 | 493.813 | 908.219 | 623.031 | 618.656 | 592.906 | 298.813 | 658.625
| 7 | 339.406 | 794.031 | 974.469 | 1054.5 | 1039.34 | 846.375 | 798.344 | 618.969 | 659.75 | 596.188 | 446.156 | 606
| 8 | 767.188 | 827.844 | 1028.59 | 1051.66 | 1039.34 | 807.469 | 841.844 | 597.969 | 670.531 | 597.25 | 689.656 | 620.813
| 9 | 780.75 | 817.375 | 955.844 | 1037.31 | 997.344 | 772.031 | 814.406 | 526.531 | 665.75 | 591.719 | 632.25 | 695.063
| 10 | 728.313 | 824.906 | 588.125 | 1044.91 | 987.656 | 784.688 | 844.781 | 543.094 | 666.281 | 584.531 | 682.313 | 700.625
| 11 | 777.219 | 803.594 | 10.75 | 1036.59 | 960.188 | 789.906 | 838.906 | 475.156 | 652.844 | 632.25 | 512.688 | 716.625
| 12 | 767.813 | 815.563 | 10.812 | 922.156 | 925.75 | 760.531 | 844.25 | 496.938 | 674.844 | 754.594 | 473.188 | 776.313
| 13 | 832.781 | 805.563 | 35.75 | 197.625 | 1102.31 | 780.563 | 830.719 | 479.625 | 666.375 | 945.094 | 674.813 | 764.938
| 14 | 747.563 | 805.063 | 11.5 | 136.156 | 1244.09 | 847.125 | 798.156 | 538.594 | 614.75 | 674.813 | 686.313 | 769.688
| 15 | 784.813 | 817.594 | 5.9062 | 164.25 | 1244.09 | 760.5 | 805.063 | 623.375 | 626.625 | 680.969 | 691.469 | 688.313
| 16 | 771.125 | 850.531 | 6.8125 | 221.875 | 1409.69 | 664.625 | 786.719 | 603.344 | 622.656 | 687.188 | 685.031 | 825.81
| 17 | 767.781 | 879.906 | 4.75 | 211.438 | 1468.5 | 768.25 | 849.188 | 613.5 | 611.75 | 659.875 | 665.625 | 782.875
| 18 | 767.813 | 878.031 | 7.25 | 230.219 | 1406.56 | 779.5 | 869.344 | 604.75 | 612.281 | 680.344 | 660.031 | 791.25
| 19 | 764.313 | 870.25 | 9.56 | 236.938 | 1340.5 | 810.969 | 766.344 | 632.125 | 631.531 | 720.25 | 656.031 | 907.375
| 20 | 770.719 | 839.781 | 8.65 | 272.906 | 1285 | 787 | 803.719 | 658.875 | 652.531 | 685.688 | 628.969 | 715.813
| 21 | 815.969 | 848.906 | 15.65 | 250.688 | 1284.75 | 862.563 | 771.5 | 621.063 | 611.063 | 708.75 | 617.75 | 732.063
| 22 | 780.75 | 880.781 | 16.87 | 296.781 | 1167.28 | 861.688 | 787.625 | 609.063 | 615.094 | 754.875 | 651.188 | 754.063
| 23 | 770.969 | 868.844 | 19.56 | 341.375 | 975.375 | 840.5 | 777.719 | 593.469 | 625.344 | 766.656 | 817.125 | 715.5
| 24 | 764.531 | 856.125 | 0.93 | 384.063 | 985.313 | 799.594 | 463.031 | 635.188 | 613.688 | 742.531 | 639.375 | 817.75
| 25 | 701.25 | 740.656 | 1204.88 | 307.875 | 931.625 | 816.719 | 507.094 | 610.781 | 606.625 | 662.031 | 795.625 | 799.875
| 26 | 800.969 | 811.906 | 1210.31 | 271.281 | 905.125 | 742.844 | 744.063 | 609.406 | 614.031 | 688.531 | 641.063 | 874.5
| 27 | 781.906 | 810.938 | 1183.84 | 233.688 | 917.219 | 519.406 | 860.219 | 641.031 | 628.969 | 684.063 | 648.063 | 793.5
| 28 | 786.531 | 808.375 | 1158.41 | 624.844 | 913.688 | 860.438 | 640.719 | 639.406 | 604.406 | 648.625 | 640.688 | 764.563
| 29 | 803.469 | 805.696 | 1192.25 | 788.469 | 927.719 | 909.938 | 686.25 |  | 624.969 | 681.344 | 763.375 | 851.313
| 30 | 764.219 | 824.031 | 1139.53 | 461.438 | 932.281 | 873.938 | 675.594 |  | 611.156 | 657 | 707.625 | 788.438
| 31 | 2022-07-01: 764.844; 2022-08-01: 860.188; 2022-10-01: 461.438; 2022-12-01: 811.125; 2023-01-01: 650.813; 2023-03-01: 604.781; 2023-05-01: 680.688
Reporting Year | Day Of Month | 2022-07-01: Volume Monitoring - Unit- kilolitres per day
|  | 2023-07-01 | 2023-08-01 | 2023-09-01 | 2023-10-01 | 2023-11-01 | 2023-12-01 | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | Comments
2023 / 2024 | 1 | 605.313 | 1012.63 | 851.625 | 675.625 | 853.68 | 873.5 | 748.406 | 763.625 | 993.063 | 980.188 | 1003.88 | 901.688
| 2 | 634.188 | 913.75 | 856.563 | 731.438 | 849.688 | 825.688 | 780.313 | 806.5 | 1017.56 | 1063.69 | 897.938 | 912.438
| 3 | 710.688 | 856.375 | 891.438 | 940.438 | 688.25 | 831.375 | 763.875 | 805.375 | 967.813 | 1117.31 | 910.75 | 910.125
| 4 | 696 | 1058.81 | 927.5 | 879.938 | 736.125 | 950 | 848.438 | 806.813 | 975.875 | 1072.13 | 891.813 | 905.313
| 5 | 732.25 | 1010.5 | 908.063 | 912.5 | 652.375 | 1031.38 | 860.563 | 821.063 | 1032.56 | 931.938 | 885.75 | 959.875
| 6 | 759.875 | 1043.25 | 909.125 | 797.688 | 695.125 | 910.375 | 891.19 | 760.875 | 989.75 | 659.375 | 910.688 | 982.813
| 7 | 758.938 | 1030.19 | 852.813 | 766.563 | 718.063 | 906 | 905.25 | 801.375 | 980.313 | 624.875 | 893.563 | 1000.38
| 8 | 759.938 | 982.25 | 727.563 | 747.375 | 831.438 | 861.188 | 856.938 | 771.375 | 946.5 | 1022.19 | 913.25 | 981.688
| 9 | 789.125 | 1026.25 | 773.188 | 962.313 | 786.813 | 833.063 | 830.25 | 842.125 | 932.313 | 997.125 | 904.5 | 980.188
| 10 | 913.188 | 862.25 | 788.375 | 1052.88 | 705.438 | 748.313 | 771.813 | 863.5 | 933.875 | 1027.56 | 804.25 | 992.063
| 11 | 826.625 | 799.438 | 945.438 | 994.25 | 749.938 | 974.188 | 936.813 | 858.125 | 936.375 | 1063.25 | 892.813 | 934.875
| 12 | 785.625 | 904.625 | 877.313 | 989.875 | 767.625 | 1040.13 | 1010.88 | 773.625 | 927.75 | 1074.25 | 810.375 | 758.563
| 13 | 702.188 | 899.25 | 828.688 | 965.5 | 839.5 | 1032.5 | 1059.38 | 945.125 | 913.375 | 1058.25 | 934.188 | 907.813
| 14 | 721.5 | 680.438 | 818.125 | 908.18 | 814.938 | 993.5 | 1089.13 | 994.375 | 951.625 | 1121.69 | 956.375 | 307.063
| 15 | 704.313 | 595.875 | 735.5 | 954.313 | 818.813 | 987.563 | 760.25 | 931.063 | 929.063 | 1119.38 | 988.875 | 0 | No discharge from 15 to 18 June 2024
| 16 | 711 | 754.813 | 728.563 | 995.625 | 823.813 | 969.375 | 739.25 | 930.938 | 885.813 | 1030.75 | 998.063 | 0
| 17 | 673.375 | 764.75 | 306.688 | 1011.81 | 794.063 | 970.813 | 1030.31 | 955.125 | 888.125 | 964.563 | 1002.19 | 0
| 18 | 675.438 | 745.688 | 482.063 | 955.625 | 756.625 | 667.875 | 928.438 | 964.313 | 960.938 | 1035.13 | 1009.63 | 0
| 19 | 697.75 | 746.438 | 733.5 | 850.438 | 855 | 728.625 | 890.75 | 925.938 | 973.75 | 1062.5 | 1017.25 | 48
| 20 | 756 | 761.25 | 830.875 | 856.313 | 840.313 | 924 | 887.563 | 945.438 | 1010.69 | 1104 | 1019.31 | 519.375
| 21 | 741.188 | 762.125 | 671.375 | 806.563 | 967.563 | 393.344 | 902.188 | 1018.56 | 993.188 | 1148.75 | 927.875 | 408.813
| 22 | 715.188 | 686.75 | 711.5 | 923.313 | 936.438 | 563.469 | 895.688 | 1058 | 995.813 | 1145.63 | 918.688 | 565.125
| 23 | 685.438 | 643.125 | 716.313 | 1079.25 | 999.563 | 574 | 910.063 | 1150.25 | 1005.13 | 1101.75 | 904.938 | 798.125
| 24 | 622.75 | 685.813 | 679.75 | 1162.69 | 940.438 | 574.094 | 898.625 | 1146.88 | 994.813 | 1132 | 920.813 | 953.813
| 25 | 609.438 | 658.125 | 740.625 | 1136.56 | 870.125 | 568.75 | 924.875 | 1151.25 | 991.125 | 1127.69 | 927.625 | 861.813
| 26 | 698.375 | 651.625 | 724.625 | 952.563 | 901.125 | 571.375 | 893.75 | 1035.69 | 977.625 | 1135.88 | 951.375 | 808.75
| 27 | 676.75 | 692.25 | 647 | 693.938 | 850.125 | 578.063 | 886.938 | 906.438 | 1015.63 | 1136.38 | 944.438 | 702.688
| 28 | 891.25 | 721.75 | 787.25 | 646 | 850.125 | 584.594 | 892.813 | 962.313 | 991.188 | 1159.88 | 897.875 | 780.938
| 29 | 905.438 | 730.375 | 697.188 | 559.438 | 919 | 554.156 | 890.063 | 987.875 | 973.5 | 1057.94 | 907.125 | 317.5
| 30 | 937.813 | 639.563 | 719.5 | 857.875 | 932.5 | 530.25 | 733.563 |  | 972.875 | 1038.81 | 900.75 | 520.313
| 31 | 2023-07-01: 1008.88; 2023-08-01: 776.625; 2023-10-01: 956.688; 2023-12-01: 543.4589; 2024-01-01: 825.063; 2024-03-01: 975.563; 2024-05-01: 924.25
Reporting Year | Day Of Month | 2023-07-01: Volume Monitoring - Unit- kilolitres per day
|  | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | 2025-01-01 | 2025-02-01 | 2025-03-01 | 2025-04-01 | 2025-05-01 | 2025-06-01 | Comments
2024 / 2025 | 1 | 764.188 | 707.438 | 935.313 | 931.063 | 791.563 | 653.5 | 738.75 | 401.625
| 2 | 737.375 | 738.563 | 803.625 | 923.125 | 764.5 | 647.938 | 692.875 | 454.563
| 3 | 754.813 | 690.313 | 860.938 | 977.75 | 1002.94 | 681.063 | 744.563 | 467.563
| 4 | 800.75 | 723.188 | 859.188 | 869.75 | 991.938 | 711.063 | 698.875 | 390.375
| 5 | 847 | 749.563 | 959.125 | 782.375 | 900 | 761.625 | 723.313 | 432.688
| 6 | 848.625 | 769.625 | 986.563 | 782.375 | 703.875 | 827.25 | 791.75 | 427.5
| 7 | 869.875 | 777.063 | 947.688 | 797.5 | 733.938 | 746.688 | 776.5 | 507.875
| 8 | 823.25 | 764.313 | 956.75 | 795.375 | 748.188 | 716 | 626.563 | 478.875
| 9 | 779 | 759.25 | 982 | 896 | 760.375 | 736 | 702.125 | 373.813
| 10 | 823.5 | 751.5 | 960.625 | 919.813 | 769.813 | 721.813 | 682 | 360.25
| 11 | 749.563 | 743.375 | 910.25 | 960.313 | 750.25 | 672 | 667.5 | 499.75
| 12 | 764 | 801.188 | 1085.5 | 1035.63 | 705.625 | 829.188 | 663.188 | 786.438
| 13 | 841.813 | 764.875 | 1229.88 | 967.375 | 630.688 | 732.688 | 674.313 | 706.625
| 14 | 820.25 | 794.5 | 1091.31 | 960.625 | 688.813 | 734.375 | 720.688 | 717.938
| 15 | 2024-07-01: 789.438; 2024-08-01: 895.938; 2024-09-01: 1174.38; 2024-10-01: 1018.81; 2024-11-01: 715.125; 2024-12-01: 571.188; 2025-02-01: 702.5 | 15/1/2025 -Data not recorded due to power outage
| 16 | 767.563 | 907.375 | 1165.38 | 877.375 | 598.5 | 451.375 | 608.563 | 693.875
| 17 | 752.688 | 849.188 | 957.438 | 872.75 | 590.688 | 733.125 | 718.188 | 780.625
| 18 | 725.313 | 828.188 | 1060.56 | 896.5 | 587.563 | 667.75 | 724.188 | 875.625
| 19 | 745.625 | 844.625 | 992.563 | 909.25 | 603.25 | 721.875 | 718.75 | 792.813
| 20 | 691.813 | 825.313 | 896.688 | 872.875 | 591.063 | 798.938 | 712.625 | 866.188
| 21 | 688.813 | 867.5 | 869.875 | 859 | 689.063 | 808.625 | 746.375 | 774.625
| 22 | 694.125 | 880.813 | 825.313 | 882.438 | 708.5 | 807.5 | 752.563 | 741.625
| 23 | 710.25 | 786.875 | 1102.31 | 711.688 | 715.813 | 794.375 | 737.938 | 754.938
| 24 | 753.188 | 805.125 | 852 | 977.813 | 692.125 | 746.563 | 747.438 | 773.313
| 25 | 706.125 | 817.188 | 1057.19 | 1000.25 | 720.625 | 757.438 | 718.188 | 780.438
| 26 | 713 | 836.438 | 872.875 | 775.063 | 783.5 | 749.438 | 387 | 771.75
| 27 | 715.188 | 844.563 | 937.563 | 935.625 | 787.375 | 759.875 | 420.75 | 753.313
| 28 | 700.313 | 968.75 | 891.125 | 994.25 | 759.063 | 724.313 | 334.75 | 756.063
| 29 | 2024-07-01: 774.125; 2024-08-01: 957.438; 2024-09-01: 905.938; 2024-10-01: 776.063; 2024-11-01: 699.438; 2024-12-01: 648.438; 2025-01-01: 369
| 30 | 2024-07-01: 766.125; 2024-08-01: 1035.88; 2024-09-01: 951.25; 2024-10-01: 852.188; 2024-11-01: 674.063; 2024-12-01: 732.375; 2025-01-01: 284.75
| 31 | 2024-07-01: 763.625; 2024-08-01: 920.875; 2024-10-01: 978.438; 2024-12-01: 769.563; 2025-01-01: 394.125

## SWTP Location Map
Note: Uncontrolled document when printed